{"text_format":"1","workbook":"xlsx","n_sheets":2,"sheets":["正面","垂直"],"not_rendered":{"charts":2,"images":1,"macros":1,"external_links":0,"defined_names":0,"comments":2,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"正面","index":0,"n_rows":38,"n_cols":8,"rows_kept":38,"cut":false,"hidden":false,"merged":[[0,3,0,8],[1,0,3,0],[5,0,10,0]]}
[null,null,null,"【条件】放射面に対する中心の受熱点の影響（4面からの影響）\n①　a、bの数値を入力してください。（黄色のセル）\n②　計算実行を押してください。\n③　10kW/㎡の距離がsに表示され、計算結果がグラフに表示されます。\n　　（赤色のセル）"]
["基本情報","a","b","s"]
[null,"[m]","[m]","[m]"]
[null,3,1.5,4.634271307045422]
[]
["計算結果","X","Y","π"]
[null,"[-]","[-]","[-]"]
[null,{"$f":"IFERROR(C4/D4,\"\")","v":0.3236754822100229},{"$f":"IFERROR(B4/D4,\"\")","v":0.6473509644200458},{"$f":"PI()","v":3.1415926535897931}]
[null,"R","F","F1","X/(1+X2)1/2","Y/(1+X2)1/2","Y/(1+Y2)1/2","X/(1+Y2)1/2"]
[null,"[kW/㎡]","[-]","[-]","[-]","[-]","[-]","[-]"]
[null,{"$f":"C11*50","v":10.000262034901084},{"$f":"D11*4","v":0.2000052406980217},{"$f":"IFERROR((1/(2*D8))*(E11*ATAN(F11)+G11*ATAN(H11)),\"\")","v":5.0001310174505424E-2},{"$f":"IFERROR(B8/(1+B8^2)^(1/2),\"\")","v":0.30794608664443518},{"$f":"IFERROR(C8/(1+B8^2)^(1/2),\"\")","v":0.61589217328887036},{"$f":"IFERROR(C8/(1+C8^2)^(1/2),\"\")","v":0.54342413099921827},{"$f":"IFERROR(B8/(1+C8^2)^(1/2),\"\")","v":0.27171206549960913}]
[]
["s","R"]
["[m]","[kW/㎡]"]
[53.354474663011992,0.1]
[16.704790333770696,1]
[11.654200892731511,2]
[9.3854972156436212,3]
[8.0154686822709955,4]
[7.0680646146305754,5]
[6.3593300854977777,6]
[5.8011238410525205,7]
[5.3451595913481871,8]
[4.9624487719799033,9]
[4.6343575371512706,10]
[4.3483031606462808,11]
[4.0954348935955114,12]
[3.8693175735764269,13]
[3.6651421766014591,14]
[3.4792306456271209,15]
[3.3087134420659488,16]
[3.1514633039464983,17]
[3.0053123173652905,18]
[2.8689494264574535,19]
[2.7411326849598403,20]
[]
[200,10]
[0,10]

{"sheet":"垂直","index":1,"n_rows":38,"n_cols":7,"rows_kept":38,"cut":false,"hidden":false,"merged":[[0,3,0,8],[1,0,3,0],[5,0,10,0]]}
[null,null,null,"【条件】放射面に対する中心の受熱点の影響（２面からの影響）\n①　a、bの数値を入力してください。（黄色のセル）\n②　計算実行を押してください。\n③　10kW/㎡の距離がsに表示され、計算結果がグラフに表示されます。\n　　（赤色のセル）"]
["基本情報","a","b","s"]
[null,"[m]","[m]","[m]"]
[null,6.5549999999999997,1.2749999999999999,3.1126886861647325]
[]
["計算結果","X","Y","π"]
[null,"[-]","[-]","[-]"]
[null,{"$f":"IFERROR(B4/C4,\"\")","v":5.1411764705882357},{"$f":"IFERROR(D4/C4,\"\")","v":2.4413244597370451},{"$f":"PI()","v":3.1415926535897931}]
[null,"R","F","F1","１/Ｙ","Ｙ/(X2+Y2)1/2","１/(X2+Ｙ2)1/2"]
[null,"[kW/㎡]","[-]","[-]","[-]","[-]","[-]"]
[null,{"$f":"C11*50","v":5.0000013298902024},{"$f":"D11*2","v":0.10000002659780405},{"$f":"IFERROR((1/(2*D8))*(ATAN(E11)-F11*ATAN(G11)),\"\")","v":5.0000013298902024E-2},{"$f":"IFERROR(1/C8,\"\")","v":0.40961372258880735},{"$f":"IFERROR(C8/($B$8^2+$C$8^2)^(1/2),\"\")","v":0.42895153395909957},{"$f":"IFERROR(1/($B$8^2+$C$8^2)^(1/2),\"\")","v":0.175704434635166}]
[]
["s","R"]
["[m]","[kW/㎡]"]
[25.277948162447814,0.1]
[10.815284737953245,1]
[8.0193106918719117,2]
[6.5980470333032928,3]
[5.6692718570986056,4]
[4.9914515413261276,5]
[4.4638592039286396,6]
[4.0362235297237996,7]
[3.6794996518513181,8]
[3.3756708559134232,9]
[3.1126937403957338,10]
[2.882139038122391,11]
[2.6778719679986827,12]
[2.4952854127219966,13]
[2.3308298886074286,14]
[2.1817123983139872,15]
[2.0456961183202211,16]
[1.9209627962141123,17]
[1.806015545418806,18]
[1.6996084797130728,19]
[1.6007829800392155,20]
[]
[200,10]
[0,10]