{"text_format":"1","workbook":"xlsx","n_sheets":2,"sheets":["正面","垂直"],"not_rendered":{"charts":2,"images":1,"macros":1,"external_links":0,"defined_names":0,"comments":2,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"正面","index":0,"n_rows":38,"n_cols":8,"rows_kept":38,"cut":false,"hidden":false,"merged":[[0,3,0,8],[1,0,3,0],[5,0,10,0]]}
[null,null,null,"【条件】放射面に対する中心の受熱点の影響（4面からの影響）\n①　a、bの数値を入力してください。（黄色のセル）\n②　計算実行を押してください。\n③　10kW/㎡の距離がsに表示され、計算結果がグラフに表示されます。\n　　（赤色のセル）"]
["基本情報","a","b","s"]
[null,"[m]","[m]","[m]"]
[null,2.5,3,9.2406795543038651]
[]
["計算結果","X","Y","π"]
[null,"[-]","[-]","[-]"]
[null,{"$f":"IFERROR(C4/D4,\"\")","v":0.32465144823713143},{"$f":"IFERROR(B4/D4,\"\")","v":0.27054287353094286},{"$f":"PI()","v":3.1415926535897931}]
[null,"R","F","F1","X/(1+X2)1/2","Y/(1+X2)1/2","Y/(1+Y2)1/2","X/(1+Y2)1/2"]
[null,"[kW/㎡]","[-]","[-]","[-]","[-]","[-]","[-]"]
[null,{"$f":"C11*100","v":10.00005068373822},{"$f":"D11*4","v":0.10000050683738219},{"$f":"IFERROR((1/(2*D8))*(E11*ATAN(F11)+G11*ATAN(H11)),\"\")","v":2.5000126709345549E-2},{"$f":"IFERROR(B8/(1+B8^2)^(1/2),\"\")","v":0.3087862097836192},{"$f":"IFERROR(C8/(1+B8^2)^(1/2),\"\")","v":0.25732184148634935},{"$f":"IFERROR(C8/(1+C8^2)^(1/2),\"\")","v":0.26115424677780863},{"$f":"IFERROR(B8/(1+C8^2)^(1/2),\"\")","v":0.3133850961333704}]
[]
["s","R"]
["[m]","[kW/㎡]"]
[97.515411603996782,0.1]
[30.7407429678425,1]
[21.621834790075294,2]
[17.554537555674521,3]
[15.119298522490736,4]
[13.446808071135814,5]
[12.208019103269445,6]
[11.238321129033631,7]
[10.452376491259947,8]
[9.79770591824958,9]
[9.2407177273541379,10]
[8.7587654927820164,11]
[8.3359460615136793,12]
[7.9607167822944422,13]
[7.6244678695060726,14]
[7.3206277667920832,15]
[7.0440811284812588,16]
[6.7907779558182524,17]
[6.55765597608438,18]
[6.3416413987050975,19]
[6.1407933671745987,20]
[]
[200,10]
[0,10]

{"sheet":"垂直","index":1,"n_rows":38,"n_cols":7,"rows_kept":38,"cut":false,"hidden":false,"merged":[[0,3,0,8],[1,0,3,0],[5,0,10,0]]}
[null,null,null,"【条件】放射面に対する中心の受熱点の影響（２面からの影響）\n①　a、bの数値を入力してください。（黄色のセル）\n②　計算実行を押してください。\n③　10kW/㎡の距離がsに表示され、計算結果がグラフに表示されます。\n　　（赤色のセル）"]
["基本情報","a","b","s"]
[null,"[m]","[m]","[m]"]
[null,6.5549999999999997,1.2749999999999999,3.1126886861647325]
[]
["計算結果","X","Y","π"]
[null,"[-]","[-]","[-]"]
[null,{"$f":"IFERROR(B4/C4,\"\")","v":5.1411764705882357},{"$f":"IFERROR(D4/C4,\"\")","v":2.4413244597370451},{"$f":"PI()","v":3.1415926535897931}]
[null,"R","F","F1","１/Ｙ","Ｙ/(X2+Y2)1/2","１/(X2+Ｙ2)1/2"]
[null,"[kW/㎡]","[-]","[-]","[-]","[-]","[-]"]
[null,{"$f":"C11*100","v":10.000002659780405},{"$f":"D11*2","v":0.10000002659780405},{"$f":"IFERROR((1/(2*D8))*(ATAN(E11)-F11*ATAN(G11)),\"\")","v":5.0000013298902024E-2},{"$f":"IFERROR(1/C8,\"\")","v":0.40961372258880735},{"$f":"IFERROR(C8/($B$8^2+$C$8^2)^(1/2),\"\")","v":0.42895153395909957},{"$f":"IFERROR(1/($B$8^2+$C$8^2)^(1/2),\"\")","v":0.175704434635166}]
[]
["s","R"]
["[m]","[kW/㎡]"]
[25.277948162447814,0.1]
[10.815284737953245,1]
[8.0193106918719117,2]
[6.5980470333032928,3]
[5.6692718570986056,4]
[4.9914515413261276,5]
[4.4638592039286396,6]
[4.0362235297237996,7]
[3.6794996518513181,8]
[3.3756708559134232,9]
[3.1126937403957338,10]
[2.882139038122391,11]
[2.6778719679986827,12]
[2.4952854127219966,13]
[2.3308298886074286,14]
[2.1817123983139872,15]
[2.0456961183202211,16]
[1.9209627962141123,17]
[1.806015545418806,18]
[1.6996084797130728,19]
[1.6007829800392155,20]
[]
[200,10]
[0,10]